MODELS COVERED:

Full Size Softeners

- CES2850M-68 Softener, 68,000 Grain

- EV9983-22 SOFTENER, 90,000 Grain

- DEV 998324 Softener, 150,000 Grain

Point of Use Softeners

- TX5600-32 Softener, 13,500 Grain

- DEV 3122-86-TEA Softener, 7,500 Grain

- TXW-CAB-5600-M-15 Softener, 15,000 Grain

COST ESTIMATE: $125-$200 per year for preventive maintenance. $125-$980 per year for salt delivery and installation (dependent on hardness of city water and Unit sales volume). Replacing resin in resin tank: $200–$900 based on softener size (5-7 years average life).

MAINTENANCE PERFORMED BY: Chick-fil-A Certified Service Agent or Everpure authorized service agent. (Operator must contact Everpure headquarters to identify local Everpure agent, based on zip code)

Contact Information

Everpure headquarters (800-842-6193)

Task Description

Preventive Maintenance: Service Agent will visit Unit once per year and will perform water analysis on site; inspect resin tank controller and brine tank for proper function; reset controller as necessary to regenerate at 2:00 a.m.; backwash flow control; and inspect Injector Nozzle and screen. Most Everpure full size softeners are equipped with water usage meters and will initiate regeneration after a specified number of gallons has been filtered. Regeneration will follow at 2:00 a.m. the next morning.

Salt Delivery: Salt Delivery Agent will deliver and load salt into softener brine tank once per month.

NOTES:

- If Service Agent determines that water softener requires additional repairs, cost of these repairs will be a Unit expense.

- The Service Agent and Salt Delivery Agent will likely be different individuals, and the tasks will be performed at different times. Salt Delivery Agents typically have limited diagnostic or repair skills.

- A full size (whole house) softener will consume approximately 100 lbs. of salt per week. A smaller Point Of Use softener uses considerably less salt.

See also SCOPE OF WORK (attached).

*     *     *     *     *     *

NOTE TO OPERATOR: Keep this page and give remaining page(s) to service agent.

Standards

- All maintenance service should be performed according to Everpure specifications.

- Service Agent must leave kitchen/mechanical room free of debris and tools.

- Service Agent must wipe down resin and brine tank surfaces.

- Service Agent must install or reinstall sticker on controller with Service Agent contact information.

- Service Agent must dispose of empty salt bags.

Warnings

Service Agent must confirm installation of check valve on cold water inlet to hot water heater. Hot water backing up through cold water inlet may migrate to water softener controller and inflict serious damage to plastic parts. Report missing check valve to Operator.

Steps

NOTE: The following instructions are intended to highlight certain steps in this procedure. Specifications developed by Everpure may require additional steps.

Preventive Maintenance

- Coordinate Unit visit with Operator or General Manager. Contact Unit at least 48 hours prior to annual visit.

- Test softener inlet and outlet water for hardness and iron levels.

- Check power supply to controller.

- Check salt and water level in brine tank. Check for possible bridging.

- Check controller and integral piping for leaks.

- Check resin tank drain line for proper flow to drain.

- Check refill to brine tank for proper flow.

- Check operation of controller bypass.

Steps (continued)

- Inspect controller and timer settings.

- Set all softeners to regenerate at 2:00 a.m.

- Set all full size softeners to regenerate based on the Chick-fil-A Equipment Calibration Specifications for the softener model (Calibration Specifications are on the last page of this form).

- Set the smaller Point Of Use softeners to regenerate every other day.

- Manually cycle control valve.

- Wipe down resin and brine tank surfaces and remove all debris from area.

- Remove and inspect Injector Nozzle and screen.  Replace if necessary.

- Manually start a regeneration cycle and verify that all steps of cycle are functioning correctly.

- Verify that sticker with contact information for Service Agent has been placed on resin tank.

- Document in writing any performance issues. Give this report to Operator or General Manager.

Salt Delivery

- Salt Delivery Agent will deliver and load salt into brine tank once per month.

- Inspect for low salt usage, leaks or controller malfunction.

- Verify that sticker with contact information for Service Agent has been placed on resin tank.

Restrictions

- Expected completion date:

- Hours work can be conducted:

- Contractor will attend inspection with Operator/manager:  YES			NO

(Reminder: All changes must be communicated to and approved in advance by Operator or General Manager of Unit.)