CFA 155 Ingram Park Mall

PROBLEM: “HI-C” NON-CARBONATED BEVERAGE HEAD DISPENSING SYRUP ONLY SOMETIMES

ROOT CAUSE: Failure of a switch or solenoid in the drink dispenser head (NOT CORRECTED- WILL NEED SERVICE CALL FROM COCA-COLA)

DETAILS ON CONDITIONS FOUND AND RESOLUTIONS:

3 drink towers at this location being fed by (1) 3/8” beverage tube from the filtration and the carbonator manifold- One dispenser head serving Hi-C non-carbonated beverage on the middle drink tower

- Attached new 3/8” beverage tube to one of the open feeds on the carbonator manifold

- Cut middle drink tower connection to the existing non-carbonated water line and capped

- Attached new line to the middle drink tower

- Proved systems for no leaks

- Flushed new and existing non-carbonated water lines and the HI-C dispenser

- The problem did not go away, even with the HI-C having a segregated 60psi line

- Informed General Manager of the restaurant and the General Manager of the Ingram Park FSU that the dispenser has a failed part that is not allowing water flow to the drink head

- This diagnosis is confirmed by the technique the store is using to make it work- if they get just syrup out of the HI-C dispenser, they flick the drinking water button a few times and this makes the water start flowing with the syrup to the HI-C

- Sampled water at the drink towers, tea brewer and sinks for chlorines and hardness

- All samples indicated correct filtration and that the filter systems are functional