## Data Collect
SURVEY DATA
Unit # | 1344
Unit Name | Southport Road FSU
Survey Date | 2009-07-07
Filter System Install Date | 2005-10-08
Operator / Manager | Matt Sewell
Unit Phone # | (317)780-7477
Service Provider Contact Info: Company Name, Contact Name. Contact Phone Primary Technician Technician Phone: | Culligan Water Conditioning (Culligan National) 6901 E 38th Street Indianapolis, IN 46226 Mark Stewart 317-591-9999 x248
Service Contract In Place Y or N | No
Service Contract Duration: From xx/xx/09 to xx/xx/09 | N/A
Description of Services & Frequency | Every 18 months they have come and checked the softener and the filters
Filtration Components: 4.5 x 20 prefilter, MF620, MF620CC etc. | MF620 (Ice Machine) MF620CC Bypass Handle with Test Rig Goulds 2A Pump
At least 3.0 Mega Pixel Photos taken using extra lighting:
Last Filter System Service Date | 2008-09-15
Salt Delivery Service Y or N | No- they get it themselves from Lowes monthly
Salt Delivery Service Frequency | N/A
Last Filter Cartrdige Change Date | 2008-09-15
Softener Type Culligan / Everpure | Culligan PVE-90- located in storage room
Softener Has Power / Is turned On Y or N | Yes
Softener In Bypass Y or N | No
Softener Calibrated to Spec Y or N | No
What is out of calibration? | fast rinse changed from 13 min to 10 min set system to regen 3x/wk
Has resin tank been rebedded? Y or N. If yes, when mm/dd/yy | No
If yes, resin tank rebedding cost? And by whom? | N/A
Salt Level in Brine Tank -Full / 3/4 / 1/2 / 1/4 / Empty | 0.75
Goulds Booster Pump Installed Y or N | Yes- located in mechanical room
Goulds Booster Pump In Operation Y or N | No
Goulds Pump Plumbed Whole House or Filtered Water Circuit Only | Whole House
Goulds Booster Pump Valves, E, F, D, and D Open Y or N, Describe | Yes- all correct
Goulds Booster Pump Controller Status Light Green or Red | Red
Goulds Booster Pump - If Red, What is Status Code (based on # blinks) | 5 blinks- short circuit
Goulds Booster Pump. What is pump running pressure (psi) | N/A
Type II Only -What is pressure gauge reading at Tea filter with softener engaged (psi) | 60 psi- see notes below
Type II Only - What is pressure gauge reading at Tea filter with softener in bypass (psi) | Did not get this reading- finally found this filter located behind a Traulsen double-door freezer- filter needs to be relocated- Operator did not know it was even there
Hardness (ppm) at Beverage Tower | 428 ppm (25 grains)
Hardness (ppm) at Tea Brewer Stop (Type II) or Softener Hose Bibb (Type II or Type III) | 17 ppm (1 grain)
Free Chlorine at Beverage Tower | Not detectable
Total Chlorine at Beverage Tower | Not detectable
Type II Only - Total chlorine at tea brewer stop. | Not detectable
Type II Only - Free chlorine at tea brewer stop. | Not detectable
Type III Only - RO Processor Making Water Y or N | N/A
Type III Only - RO Processor Flow Rate to Holding Tank (gpm) | N/A
Type III Only - RO Processor Permeate Water TDS | N/A
Type III Only - RO Processor Waste Water Flow Rate (gpm) | N/A
Type III Only - RO Processor Waste Water TDS | N/A
Type III Only - Goulds Delivery Pump In Operation Y or N | N/A
Type III Only - Goulds Delivery Pump Controller Status Light Green or Red | N/A
Type III Only - Goulds Delivery Pump. If Red, What is Status Code (based on # blinks) | N/A
Type III Only - Goulds Delivery Pump. What is pump running pressure (psi) | N/A
City Water TDS | 376 ppm
City Water Hardness (ppm) | 393 ppm (23 grains)
City Water Total Chlorine | 1.5 mg/L
City Water Free Chlorine | 0.4 mg/L
Significant Notes About Location | 1. Tea brewers are plumbed with bev tubing and galvanized (corroded fittings) 2. Booster pump has short circuit- could be pump motor, could be wiring- will need to check 3. Filter for ice machine removed- evident by filter wrench still attached to line behind machine- replumbed without filter, backflow preventer and soft copper tubing 4. Abandoned shake machine located in mechanical room