## Data Collect
SURVEY DATA
Unit # | 1413
Unit Name | Greenwood FSU
Survey Date | 2009-07-07
Filter System Install Date | 2005-10-26
Operator / Manager | Rick Johnson
Unit Phone # | (317)888-8100
Service Provider Contact Info: Company Name, Contact Name. Contact Phone Primary Technician Technician Phone: | Culligan Water Conditioning 6901 E 38th Street Indianapolis, IN 46226 (317)885-0444
Service Contract In Place Y or N | No
Service Contract Duration: From xx/xx/09 to xx/xx/09 | No- last salt delivery on 7/1/09
Description of Services & Frequency | Salt Delivery Only
Filtration Components: 4.5 x 20 prefilter, MF620, MF620CC etc. | MF620 (Coffee/Tea) MF620CC Bypass Handle with Test Rig Goulds 2A Pump
At least 3.0 Mega Pixel Photos taken using extra lighting:
Last Filter System Service Date | 2007-11-05
Salt Delivery Service Y or N | Yes
Salt Delivery Service Frequency | Monthly- 600 lbs
Last Filter Cartridge Change Date | 2007-11-05
Softener Type Culligan / Everpure | Culligan PVE-90B- brine tank is located in storage room, separate from the resin tank
Softener Has Power / Is turned On Y or N | Yes
Softener In Bypass Y or N | No
Softener Calibrated to Spec Y or N | No
What is out of calibration? | Back wash was at 8 min.- now at 10 Fast rinse was at 13 min.- now at 11
Has resin tank been rebedded? Y or N. If yes, when mm/dd/yy | No
If yes, resin tank rebedding cost? And by whom? | N/A
Salt Level in Brine Tank -Full / 3/4 / 1/2 / 1/4 / Empty | Empty (still briny)
Goulds Booster Pump Installed Y or N | Yes
Goulds Booster Pump In Operation Y or N | Yes
Goulds Pump Plumbed Whole House or Filtered Water Circuit Only | Whole House
Goulds Booster Pump Valves, E, F, D, and D Open Y or N, Describe | Yes- all open and plumbed correctly
Goulds Booster Pump Controller Status Light Green or Red | Green
Goulds Booster Pump - If Red, What is Status Code (based on # blinks) | N/A
Goulds Booster Pump. What is pump running pressure (psi) | 80 psi- taken from filter bypass gauge- gauge at booster pump is not functional
Type II Only -What is pressure gauge reading at Tea filter with softener engaged (psi) | 78 psi
Type II Only - What is pressure gauge reading at Tea filter with softener in bypass (psi) | 76 psi
Hardness (ppm) at Beverage Tower | 342 ppm (20 grains)
Hardness (ppm) at Tea Brewer Stop (Type II) or Softener Hose Bibb (Type II or Type III) | Not detectable
Free Chlorine at Beverage Tower | Not detectable
Total Chlorine at Beverage Tower | Not detectable
Type II Only - Total chlorine at tea brewer stop. | Not detectable
Type II Only - Free chlorine at tea brewer stop. | Not detectable
Type III Only - RO Processor Making Water Y or N | N/A
Type III Only - RO Processor Flow Rate to Holding Tank (gpm) | N/A
Type III Only - RO Processor Permeate Water TDS | N/A
Type III Only - RO Processor Waste Water Flow Rate (gpm) | N/A
Type III Only - RO Processor Waste Water TDS | N/A
Type III Only - Goulds Delivery Pump In Operation Y or N | N/A
Type III Only - Goulds Delivery Pump Controller Status Light Green or Red | N/A
Type III Only - Goulds Delivery Pump. If Red, What is Status Code (based on # blinks) | N/A
Type III Only - Goulds Delivery Pump. What is pump running pressure (psi) | N/A
City Water TDS | 416 ppm
City Water Hardness (ppm) | 376.2 ppm (22 grains)
City Water Total Chlorine | 0.6 mg/L
City Water Free Chlorine | 0.5 mg/L
Significant Notes About Location | 1. Ice Machine is not filtered 2. Booster pump gauge is not functional 3. Kitchen ceiling needs repairs by fryline- grid collapsing and rusted 4. Dumpster hose bib has underground break- needs trenched and repaired- break most likely under asphalt