## Data Collect
SURVEY DATA
Unit # | 1439
Unit Name | Jefferson Pointe FSU
Survey Date | 2009-07-15
Filter System Install Date | 2005-10-16
Operator / Manager | Jeff Hoffman
Unit Phone # | (260) 436-8203
Service Provider Contact Info: Company Name, Contact Name. Contact Phone Primary Technician Technician Phone: | None
Service Contract In Place Y or N | N/A
Service Contract Duration: From xx/xx/09 to xx/xx/09 | N/A
Description of Services & Frequency | N/A
Filtration Components: 4.5 x 20 prefilter, MF620, MF620CC etc. | 4.5 x 20 prefilter MF620CC IcePRO S-10 CoffeePRO 10 Bypass Handle with Test Rig Goulds 1A Pump
At least 3.0 Mega Pixel Photos taken using extra lighting:
Last Filter System Service Date | 2009-02-09
Salt Delivery Service Y or N | N/A
Salt Delivery Service Frequency | N/A
Last Filter Cartridge Change Date | 2009-02-09
Softener Type Culligan / Everpure | N/A
Softener Has Power / Is turned On Y or N | N/A
Softener In Bypass Y or N | N/A
Softener Calibrated to Spec Y or N | N/A
What is out of calibration? | N/A
Has resin tank been rebedded? Y or N. If yes, when mm/dd/yy | N/A
If yes, resin tank rebedding cost? And by whom? | N/A
Salt Level in Brine Tank -Full / 3/4 / 1/2 / 1/4 / Empty | N/A
Goulds Booster Pump Installed Y or N | Yes
Goulds Booster Pump In Operation Y or N | Yes
Goulds Pump Plumbed Whole House or Filtered Water Circuit Only | Filtered Water Circuit Only
Goulds Booster Pump Valves, E, F, D, and D Open Y or N, Describe | Yes
Goulds Booster Pump Controller Status Light Green or Red | Green
Goulds Booster Pump - If Red, What is Status Code (based on # blinks) | N/A
Goulds Booster Pump. What is pump running pressure (psi) | 80 psi
Type II Only -What is pressure gauge reading at Tea filter with softener engaged (psi) | N/A
Type II Only - What is pressure gauge reading at Tea filter with softener in bypass (psi) | N/A
Hardness (ppm) at Beverage Tower | 103 ppm (6 grains)
Hardness (ppm) at Tea Brewer Stop (Type II) or Softener Hose Bibb (Type II or Type III) | N/A
Free Chlorine at Beverage Tower | Not detectable
Total Chlorine at Beverage Tower | Not detectable
Type II Only - Total chlorine at tea brewer stop. | Not detectable
Type II Only - Free chlorine at tea brewer stop. | Not detectable
Type III Only - RO Processor Making Water Y or N | N/A
Type III Only - RO Processor Flow Rate to Holding Tank (gpm) | N/A
Type III Only - RO Processor Permeate Water TDS | N/A
Type III Only - RO Processor Waste Water Flow Rate (gpm) | N/A
Type III Only - RO Processor Waste Water TDS | N/A
Type III Only - Goulds Delivery Pump In Operation Y or N | N/A
Type III Only - Goulds Delivery Pump Controller Status Light Green or Red | N/A
Type III Only - Goulds Delivery Pump. If Red, What is Status Code (based on # blinks) | N/A
Type III Only - Goulds Delivery Pump. What is pump running pressure (psi) | N/A
City Water TDS | 156 ppm
City Water Hardness (ppm) | 120 ppm (7 grains)
City Water Total Chlorine | 1.0 mg/L
City Water Free Chlorine | 0.7 mg/L
Significant Notes About Location