## Data Collect
SURVEY DATA
Unit # | 1473
Unit Name | Circle Centre Mall
Survey Date | 2009-07-21
Filter System Install Date | 2005-10-07
Operator / Manager | Sam Hartman
Unit Phone # | (317)822-8501
Service Provider Contact Info: Company Name, Contact Name. Contact Phone Primary Technician Technician Phone: | None
Service Contract In Place Y or N | N/A
Service Contract Duration: From xx/xx/09 to xx/xx/09 | N/A
Description of Services & Frequency | N/A
Filtration Components: 4.5 x 20 prefilter, MF620, MF620CC etc. | MF620CC MF620 Bypass Handle with Test Rig Goulds 2A Pump
At least 3.0 Mega Pixel Photos taken using extra lighting:
Last Filter System Service Date | 2009-04-15
Salt Delivery Service Y or N | No
Salt Delivery Service Frequency | Operator is buying it himself monthly- system was completely empty during visit in June- now has salt
Last Filter Cartridge Change Date | 2009-04-15
Softener Type Culligan / Everpure | Culligan PVE-45
Softener Has Power / Is turned On Y or N | Yes
Softener In Bypass Y or N | No
Softener Calibrated to Spec Y or N | No
What is out of calibration? | Time of day changed from 3:38pm to 4:40pm Back wash changed from 7 to 10 minutes Fast rinse changed from 7 to 6 minutes Day of week changed from Friday to Tuesday Regen changed from 3 to 4 days/week
Has resin tank been rebedded? Y or N. If yes, when mm/dd/yy | No
If yes, resin tank rebedding cost? And by whom? | N/A
Salt Level in Brine Tank -Full / 3/4 / 1/2 / 1/4 / Empty | 0.25
Goulds Booster Pump Installed Y or N | Yes
Goulds Booster Pump In Operation Y or N | Yes
Goulds Pump Plumbed Whole House or Filtered Water Circuit Only | Whole House
Goulds Booster Pump Valves, E, F, D, and D Open Y or N, Describe | Yes
Goulds Booster Pump Controller Status Light Green or Red | Green
Goulds Booster Pump - If Red, What is Status Code (based on # blinks) | N/A
Goulds Booster Pump. What is pump running pressure (psi) | 80 psi
Type II Only -What is pressure gauge reading at Tea filter with softener engaged (psi) | 55 psi
Type II Only - What is pressure gauge reading at Tea filter with softener in bypass (psi) | 56 psi
Hardness (ppm) at Beverage Tower | 308 ppm (18 grains)
Hardness (ppm) at Tea Brewer Stop (Type II) or Softener Hose Bibb (Type II or Type III) | 17 ppm (1 grain)
Free Chlorine at Beverage Tower | Not detectable
Total Chlorine at Beverage Tower | Not detectable
Type II Only - Total chlorine at tea brewer stop. | 0.1 mg/L
Type II Only - Free chlorine at tea brewer stop. | Not detectable
Type III Only - RO Processor Making Water Y or N | N/A
Type III Only - RO Processor Flow Rate to Holding Tank (gpm) | N/A
Type III Only - RO Processor Permeate Water TDS | N/A
Type III Only - RO Processor Waste Water Flow Rate (gpm) | N/A
Type III Only - RO Processor Waste Water TDS | N/A
Type III Only - Goulds Delivery Pump In Operation Y or N | N/A
Type III Only - Goulds Delivery Pump Controller Status Light Green or Red | N/A
Type III Only - Goulds Delivery Pump. If Red, What is Status Code (based on # blinks) | N/A
Type III Only - Goulds Delivery Pump. What is pump running pressure (psi) | N/A
City Water TDS | 428 ppm
City Water Hardness (ppm) | 325 ppm (19 grains)
City Water Total Chlorine | 2.0 mg/L
City Water Free Chlorine | 1.1 mg/L
Significant Notes About Location | 1. No filter in place for ice machine 2. Booster pump has no pressure relief valve- top of pump outlet tee is capped