## Data Collect
SURVEY DATA
Unit # | 1602
Unit Name | Mishawaka Main Street FSU
Survey Date | 2009-07-20
Filter System Install Date | 2005-10-18
Operator / Manager | Kathy Wonderly
Unit Phone # | (574) 277-0222
Service Provider Contact Info: Company Name, Contact Name. Contact Phone Primary Technician Technician Phone: | Culligan South Bend (574)807-9756 Tim Mellen/Jack Strickland
Service Contract In Place Y or N | No
Service Contract Duration: From xx/xx/09 to xx/xx/09 | N/A
Description of Services & Frequency | Salt delivery only- every 2 weeks
Filtration Components: 4.5 x 20 prefilter, MF620, MF620CC etc. | MF620CC MF620 Bypass Handle with Test Rig Goulds 2A Pump
At least 3.0 Mega Pixel Photos taken using extra lighting:
Last Filter System Service Date | 2009-07-01
Salt Delivery Service Y or N | Yes
Salt Delivery Service Frequency | Every 2 weeks
Last Filter Cartridge Change Date | 2009-07-01
Softener Type Culligan / Everpure | Culligan
Softener Has Power / Is turned On Y or N | Yes
Softener In Bypass Y or N | No
Softener Calibrated to Spec Y or N | No
What is out of calibration? | Time of regen changed from 1am to 2am Fast rinse changed from 10 to 11 minutes Regeneration changed from 7 to 4 days/week
Has resin tank been rebedded? Y or N. If yes, when mm/dd/yy | No
If yes, resin tank rebedding cost? And by whom? | N/A
Salt Level in Brine Tank -Full / 3/4 / 1/2 / 1/4 / Empty | 0.5
Goulds Booster Pump Installed Y or N | Yes
Goulds Booster Pump In Operation Y or N | Yes
Goulds Pump Plumbed Whole House or Filtered Water Circuit Only | Whole House
Goulds Booster Pump Valves, E, F, D, and D Open Y or N, Describe | Yes
Goulds Booster Pump Controller Status Light Green or Red | Green
Goulds Booster Pump - If Red, What is Status Code (based on # blinks) | N/A
Goulds Booster Pump. What is pump running pressure (psi) | 80 psi
Type II Only -What is pressure gauge reading at Tea filter with softener engaged (psi) | 60 psi
Type II Only - What is pressure gauge reading at Tea filter with softener in bypass (psi) | 60 psi
Hardness (ppm) at Beverage Tower | 359 ppm (21 grains)
Hardness (ppm) at Tea Brewer Stop (Type II) or Softener Hose Bibb (Type II or Type III) | 0 ppm (0 grains)
Free Chlorine at Beverage Tower | Not detectable
Total Chlorine at Beverage Tower | Not detectable
Type II Only - Total chlorine at tea brewer stop. | 0.1 mg/L
Type II Only - Free chlorine at tea brewer stop. | 0.1 mg/L
Type III Only - RO Processor Making Water Y or N | N/A
Type III Only - RO Processor Flow Rate to Holding Tank (gpm) | N/A
Type III Only - RO Processor Permeate Water TDS | N/A
Type III Only - RO Processor Waste Water Flow Rate (gpm) | N/A
Type III Only - RO Processor Waste Water TDS | N/A
Type III Only - Goulds Delivery Pump In Operation Y or N | N/A
Type III Only - Goulds Delivery Pump Controller Status Light Green or Red | N/A
Type III Only - Goulds Delivery Pump. If Red, What is Status Code (based on # blinks) | N/A
Type III Only - Goulds Delivery Pump. What is pump running pressure (psi) | N/A
City Water TDS | 405 ppm
City Water Hardness (ppm) | 376 ppm (22 grains)
City Water Total Chlorine | 0.6 mg/L
City Water Free Chlorine | 0.5 mg/L
Significant Notes About Location | 1. No filtration on Ice Machine 2. Gauges on bypass handle not reading correctly- outlet pressure not functioning at all- inlet pressure reading 10 psi under pump gauge