CFA 1776 Ingram Park FSU

PROBLEM: BLACK FLECKS IN NON-CARBONATED PRODUCTS AT THE DRINK TOWERS

ROOT CAUSE: Cartridge failure allowing carbon into system

DETAILS ON CONDITIONS FOUND AND RESOLUTIONS:

Non-carb products not being fed by correct filtration- should have been same filter set (MF620CC) as carbonated products

- Corrected by removing from incorrect source and connecting to correct source

- Flushed all drinking water and non-carbonated drinks at the drink towers to purge all carbon flecks

Non-carb products being fed by Tea/Coffee filtration which includes that it is softened water

- Removed incorrect connection and capped

Tea/Coffee filtration (MF620) cartridge failed and coated with thick green paste 8-12” deep from bottom of cartridge bowl

- Removed failed cartridge and disposed

- Cleaned and sanitized cartridge bowl

- Reinstalled empty cartridge bowl to MF620 filter head

- Contacted Strategic Equipment to send new 101-300 cartridge

Far right filter head on MF620CC system leaking through the pressure relief valve

- Tried repair by tightening set screw on pressure relief valve- did not correct leak due to the opening now being oblong

- Contacted Strategic Equipment to send new filter head- they recommend a new set of 3 as disassembly of the triple filtration has proved to be a problem

- System will be sent to the store and a plumber will install

Culligan 3 cu. Ft. softener MVP control head flowing to drain constantly

- Placed service call to Culligan SA (salt delivery provider) on 9/2/09

- Service tech on site on 9/3/09- replaced failed solenoid and seal kit