## Data Collect
SURVEY DATA
Unit # | 1939
Unit Name | Westfield FSU
Survey Date | 2009-07-09
Filter System Install Date | 2006-12-14
Operator / Manager | Troy Buchanan
Unit Phone # | (317) 815-9465
Service Provider Contact Info: Company Name, Contact Name. Contact Phone Primary Technician Technician Phone: | Aqua Systems 7785 East US Hwy 36 Avon, IN 46123 800-447-5582
Service Contract In Place Y or N | No, but do have account with them
Service Contract Duration: From xx/xx/09 to xx/xx/09 | N/A
Description of Services & Frequency | Salt Delivery
Filtration Components: 4.5 x 20 prefilter, MF620, MF620CC etc. | Type II Panel with Goulds 2A Pump. MF620CC, MF620
At least 3.0 Mega Pixel Photos taken using extra lighting:
Last Filter System Service Date | None since new
Salt Delivery Service Y or N | Yes
Salt Delivery Service Frequency | Monthly- quantity differs
Last Filter Cartridge Change Date | None since new
Softener Type Culligan / Everpure | Culligan PVE-90
Softener Has Power / Is turned On Y or N | Yes
Softener In Bypass Y or N | No
Softener Calibrated to Spec Y or N | No
What is out of calibration? | time of regen changed from 11:30pm to 2:00am backwash time changed from 8 min to 10 min fast rinse changed from 7 min to 11 min regen changed from 3/wk to 5/wk (M,W,Th,F,Sa)
Has resin tank been rebedded? Y or N. If yes, when mm/dd/yy | No
If yes, resin tank rebedding cost? And by whom? | N/A
Salt Level in Brine Tank -Full / 3/4 / 1/2 / 1/4 / Empty | Full
Goulds Booster Pump Installed Y or N | Yes
Goulds Booster Pump In Operation Y or N | Yes
Goulds Pump Plumbed Whole House or Filtered Water Circuit Only | Whole House
Goulds Booster Pump Valves, E, F, D, and D Open Y or N, Describe | Yes
Goulds Booster Pump Controller Status Light Green or Red | Green
Goulds Booster Pump - If Red, What is Status Code (based on # blinks) | N/A
Goulds Booster Pump. What is pump running pressure (psi) | 85 psi (read from filter bypass gauge due to booster pump gauge not functioning)
Type II Only -What is pressure gauge reading at Tea filter with softener engaged (psi) | 70 psi
Type II Only - What is pressure gauge reading at Tea filter with softener in bypass (psi) | 80 psi
Hardness (ppm) at Beverage Tower | 393 ppm (23 grains)
Hardness (ppm) at Tea Brewer Stop (Type II) or Softener Hose Bibb (Type II or Type III) | 17 ppm (1 grain)
Free Chlorine at Beverage Tower | Not detectable
Total Chlorine at Beverage Tower | Not detectable
Type II Only - Total chlorine at tea brewer stop. | Not detectable
Type II Only - Free chlorine at tea brewer stop. | Not detectable
Type III Only - RO Processor Making Water Y or N | N/A
Type III Only - RO Processor Flow Rate to Holding Tank (gpm) | N/A
Type III Only - RO Processor Permeate Water TDS | N/A
Type III Only - RO Processor Waste Water Flow Rate (gpm) | N/A
Type III Only - RO Processor Waste Water TDS | N/A
Type III Only - Goulds Delivery Pump In Operation Y or N | N/A
Type III Only - Goulds Delivery Pump Controller Status Light Green or Red | N/A
Type III Only - Goulds Delivery Pump. If Red, What is Status Code (based on # blinks) | N/A
Type III Only - Goulds Delivery Pump. What is pump running pressure (psi) | N/A
City Water TDS | 365 ppm
City Water Hardness (ppm) | 393 ppm (23 grains)
City Water Total Chlorine | 1.1 mg/L
City Water Free Chlorine | 0.6 mg/L
Significant Notes About Location | 1. No filtration for Ice Machine 2. Booster pump gauge is not functional