## Sheet1
2050 | Hawks Creek FSU | Dusty Russell (817)735-8225 | S06C-R 05.9 | Type 1 w/POU | WFH EQUIPMENT: NONE
TRACKED THROUGH PO's: GOULDS WH PUMP PANEL, 6-STOP MANIFOLD, EV 7500G SOFTENER, 4.5x20 PF, MF620CC, COFFEEPRO-10, ICEPRO-10
ACTUAL: GOULDS (NPE) WH PUMP PANEL, 6-STOP MANIFOLD, EV 7500G SOFTENER (5600 SKIPPER WHEEL), 4.5x20 PF, MF620CC, COFFEEPRO-10, ICEPRO-10
12/3/11- found POU softener bypassed, 4.5x20 prefilter bypassed, no history of cartridges ever being purchased through Strategic (confirmed with Robert 12/5)- filters for drink towers, filtered water faucet and brewers are all fouled (40-50 psi drop, Dynamic drop to zero psi)
Brine line from controller connected to the Brine Tank drain line- connected it to the brine float assembly (ferrule was still there)
Started a manual regeneration and was shot by water from the drain line- bev tubing zip-tied to sink legs and sort of aimed at a floor drain- I improved the zip-ties and directed the drainline to the floor drain
I suspect that someone thought the softener was broken with drain water spraying out from under the sink
Softener appears to function correctly- ran it through a quick cycle, then disconnected the line from the tea brewer and flushed for 5 minutes
Softener is set for regeneration once every 6 days and has salt in it
MF620CC system is blocked, showing 90 psi in, static 40-50 psi out, dynamic 0 psi out
When put in bypass, showing 90 psi in, static 90 psi out
4.5x20 Prefilter has been in bypass since new- cartridge is still pristine- filter is now in use
Robert McWhorter is ready to ship as soon as the Restaurant calls