## Data Collect
SURVEY DATA
Unit # | 2114
Unit Name | Beavercreek FSU
Survey Date | 2009-07-13
Filter System Install Date | 2007-04-05
Operator / Manager | Jason Ramsey
Unit Phone # | (937)320-1228
Service Provider Contact Info: Company Name, Contact Name. Contact Phone Primary Technician Technician Phone: | None
Service Contract In Place Y or N | No
Service Contract Duration: From xx/xx/09 to xx/xx/09 | N/A
Description of Services & Frequency | N/A
Filtration Components: 4.5 x 20 prefilter, MF620, MF620CC etc. | Everpure CB-20-124E Pre Filter (cartridge CC1E) Everpure CB-20-124E Post Filter (cartridge CC1E) Everpure SR-X 12" Everpure MRS 700 Combi RO Processor
At least 3.0 Mega Pixel Photos taken using extra lighting:
Last Filter System Service Date | N/A
Salt Delivery Service Y or N | Yes- delivered with MBM food orders
Salt Delivery Service Frequency | Rarely- Operator was not aware that softener was not regenerating due to flow meter failure
Last Filter Cartridge Change Date | N/A
Softener Type Culligan / Everpure | Everpure 3 cubic ft with ces 2850 controller and flow meter
Softener Has Power / Is turned On Y or N | Yes
Softener In Bypass Y or N | No
Softener Calibrated to Spec Y or N | No
What is out of calibration? | Brine Refill Time changed from 13 min to 8 min Regen- cable and flow meter not functional
Has resin tank been rebedded? Y or N. If yes, when mm/dd/yy | No
If yes, resin tank rebedding cost? And by whom? | N/A
Salt Level in Brine Tank -Full / 3/4 / 1/2 / 1/4 / Empty | 0.5
Goulds Booster Pump Installed Y or N | Yes
Goulds Booster Pump In Operation Y or N | Yes
Goulds Pump Plumbed Whole House or Filtered Water Circuit Only | Whole House
Goulds Booster Pump Valves, E, F, D, and D Open Y or N, Describe | Yes
Goulds Booster Pump Controller Status Light Green or Red | Green
Goulds Booster Pump - If Red, What is Status Code (based on # blinks) | N/A
Goulds Booster Pump. What is pump running pressure (psi) | 80 psi
Type II Only -What is pressure gauge reading at Tea filter with softener engaged (psi) | Softener not operating at time of survey- will enter data when delivery pump is replaced and softener is repaired
Type II Only - What is pressure gauge reading at Tea filter with softener in bypass (psi) | Softener not operating at time of survey- will enter data when delivery pump is replaced and softener is repaired
Hardness (ppm) at Beverage Tower | 393 ppm (23 grains)
Hardness (ppm) at Tea Brewer Stop (Type II) or Softener Hose Bibb (Type II or Type III) | Softener not operating at time of survey- will enter data when delivery pump is replaced and softener is repaired
Free Chlorine at Beverage Tower | Not detectable
Total Chlorine at Beverage Tower | Not detectable
Type II Only - Total chlorine at tea brewer stop. | Not detectable
Type II Only - Free chlorine at tea brewer stop. | Not detectable
Type III Only - RO Processor Making Water Y or N | No- was bypassed and delivery pump shut down on arrival- corrected and running
Type III Only - RO Processor Flow Rate to Holding Tank (gpm) | .375 gpm- will calibrate blend when new delivery pump installed
Type III Only - RO Processor Permeate Water TDS | 88 ppm
Type III Only - RO Processor Waste Water Flow Rate (gpm) | .938 gpm- will calibrate blend when new delivery pump installed
Type III Only - RO Processor Waste Water TDS | 487 ppm
Type III Only - Goulds Delivery Pump In Operation Y or N | No- delivery pump shut down on arrival- corrected and running
Type III Only - Goulds Delivery Pump Controller Status Light Green or Red | Pump shut off electrically and bypassed on arrival- now displaying Green
Type III Only - Goulds Delivery Pump. If Red, What is Status Code (based on # blinks) | N/A
Type III Only - Goulds Delivery Pump. What is pump running pressure (psi) | 80 psi- will reenter new data when pump is replaced
City Water TDS | 380 ppm
City Water Hardness (ppm) | 393 ppm (23 grains)
City Water Total Chlorine | 1.6 mg/L
City Water Free Chlorine | 1.3 mg/L
Significant Notes About Location | 1. RO Delivery pump was shutdown on arrival and RO bypassed due to reported leak between casing and nose of delivery pump- Operator reported that someone tightened the bolts last week but did not restart the system- ran system for 1 hr while at store with no leak(s) evident 2. Softener flow meter cable and internal gearings are not functional- replacement parts are being ordered and will be installed by Mark Barranco- Closing Manager was instructed on correct method of starting regeneration cycle manually- he will train other closing Managers and they will manually regenerate the softener every night until the flow meter is repaired 3. Will have to return to store to verify repairs, resample applications and calibrate RO properly 4. Incorrect filtration at ice machine- there is a polyphosphate feeder installed