## Data Collect
SURVEY DATA
Unit # | 2158
Unit Name | Coral Ridge Mall
Survey Date | 2009-07-17
Filter System Install Date | 2007-04-19
Operator / Manager | Bob Schmidt
Unit Phone # | (319) 625-2020
Service Provider Contact Info: Company Name, Contact Name. Contact Phone Primary Technician Technician Phone: | A2Z Mechanical Contractors, Inc. 4218 Yvette Street SW Iowa City, IA 52240 Mike Jones 319-351-2743 Scott Jones (same #)
Service Contract In Place Y or N | Yes
Service Contract Duration: From xx/xx/09 to xx/xx/09 | 4/09 through 4/10
Description of Services & Frequency | Salt Delivery- monthly RO System Cartridge Replacement- Quarterly Prefilter Cartridge Replacement- as needed (total of 4)
Filtration Components: 4.5 x 20 prefilter, MF620, MF620CC etc. | Everpure 2 cu. ft Softener Everpure MRS 700 Combi RO System Everpure Carbon Post Filter (3) Everpure Prefilters RO Pump Board Goulds 1A Pump Goulds 2A Pump
At least 3.0 Mega Pixel Photos taken using extra lighting:
Last Filter System Service Date | 2009-04-27
Salt Delivery Service Y or N | Yes
Salt Delivery Service Frequency | Monthly
Last Filter Cartridge Change Date | 2009-04-27
Softener Type Culligan / Everpure | Everpure 2 cubic ft.
Softener Has Power / Is turned On Y or N | Yes
Softener In Bypass Y or N | No
Softener Calibrated to Spec Y or N | No
What is out of calibration? | time of day changed from 5pm to 2:30pm gallons/regen changed from 9,000 to 1400
Has resin tank been rebedded? Y or N. If yes, when mm/dd/yy | No
If yes, resin tank rebedding cost? And by whom? | N/A
Salt Level in Brine Tank -Full / 3/4 / 1/2 / 1/4 / Empty | Full
Goulds Booster Pump Installed Y or N | Yes
Goulds Booster Pump In Operation Y or N | No- yes now (but too late to save solenoid #1 on RO system)
Goulds Pump Plumbed Whole House or Filtered Water Circuit Only | Whole House
Goulds Booster Pump Valves, E, F, D, and D Open Y or N, Describe | Yes
Goulds Booster Pump Controller Status Light Green or Red | Red
Goulds Booster Pump - If Red, What is Status Code (based on # blinks) | 1 blink- low water/loss of prime (system reset and ran for 4+ hours while I was still there
Goulds Booster Pump. What is pump running pressure (psi) | 32 psi on arrival- 85 psi now
Type II Only -What is pressure gauge reading at Tea filter with softener engaged (psi) | N/A
Type II Only - What is pressure gauge reading at Tea filter with softener in bypass (psi) | N/A
Hardness (ppm) at Beverage Tower | 462 ppm (27 grains)
Hardness (ppm) at Tea Brewer Stop (Type II) or Softener Hose Bibb (Type II or Type III) | 445 ppm (26 grains)
Free Chlorine at Beverage Tower | Not detectable
Total Chlorine at Beverage Tower | Not detectable
Type II Only - Total chlorine at tea brewer stop. | Not detectable
Type II Only - Free chlorine at tea brewer stop. | Not detectable
Type III Only - RO Processor Making Water Y or N | No- filling holding tank, but not with RO processed water
Type III Only - RO Processor Flow Rate to Holding Tank (gpm) | 0.47 gpm
Type III Only - RO Processor Permeate Water TDS | Not measured- system in failure
Type III Only - RO Processor Waste Water Flow Rate (gpm) | Not measured- system in failure
Type III Only - RO Processor Waste Water TDS | Not measured- system in failure
Type III Only - Goulds Delivery Pump In Operation Y or N | Yes
Type III Only - Goulds Delivery Pump Controller Status Light Green or Red | Green
Type III Only - Goulds Delivery Pump. If Red, What is Status Code (based on # blinks) | N/A
Type III Only - Goulds Delivery Pump. What is pump running pressure (psi) | 80 psi
City Water TDS | 609 ppm
City Water Hardness (ppm) | 479 ppm (28 grains)
City Water Total Chlorine | 1.0 mg/L
City Water Free Chlorine | 0.8 mg/L
Significant Notes About Location | wow- see extensive notes below
| BOOSTER PUMP NOTES | On arrival, store booster pump was not running, RO system was not removing any TDS (no water being RO treated by membranes), softener not regenerated or providing softened water
booster pump is located by itself in a smaller mezzanine storage area above back door- not visible unless you are up there- I am not surprised that it was not noticed, other than a 45-50 psi drop in pressure!
Booster pump was in fault for low water/loss of prime (my guess is mall work done on plumbing at some point starved it out and forced the fault)
Reset booster pump and it started right back up and ran for the next 5 hours I was at location
| RO SYSTEM NOTES | RO system- membrane cartridges were hot to the touch (maybe 5-10 seconds of grabbing one before you had to remove your hand)- not sure, but I would think that can't be good for them!
I think solenoid has failed and been replaced before- it had wire nuts connecting it to the clip- solenoid #2 does not- no splicing
No water getting to the RO section of the MRS 700 Combi system- after checking, Solenoid #1 has failed in the closed position, stopping water from reaching the internal PROCON pump and the RO membrane cartridges- proved solenoid failure electrically- also mechanically proved PROCON pump is still functional.
recommend relay on booster pump failure that shuts down MRS 700 Combi w/audible alarm- also recommend strategically placed 4" pressure gauge for booster pumped pressure- visual check
Turned off MRS 700 Combi system- Bypassed RO system at the board- removed failed solenoid- A2Z Mechanical has failed solenoid and have already contacted Tom Haagen (?) from Everpure for part replacement- will install on receipt of replacement
Will have to be calibrated once we get RO membranes functioning- I will recommend draining RO holding tank (why not, it has 600 ppm of TDS already)- calibrate permeate and discharge blending- test tea brewer for hardness- also test drink towers to prove it is running non-softened water (or is it running softened?)-
replace membranes due to heat/600+ ppm TDS/2+ yrs old?
| SOFTENER NOTES | Softener not functioning on arrival- bev towers, tea and ice machine (delivery, not melted) all showed hardness equal to city water
Softener is positioned where you can't really see the control head- I used the camera to verify and change settings necessary to reach CFA calibration specs
A2Z reported that they had replaced the flow meter cable due to broken end at the flow meter- I think it was not pushed in completely and had not been regenerating- I manually started a regen cycle to test electrical and mechanical functions, and it will regen- inserted cable end fully into flow meter and I believe it will regen now
by the way, are you aware that a 2 cubic ft softener was installed there? City water tested at 479 ppm hardness (28 grains)
will instruct that monthly salt deliveries include TDS check on RO permeate- hardness test from tea brewer dilution tube (anything else?)